SECTION 14202

ELEVATORS AND LIFTS

Display hidden notes to specifier. (Don't know how? Click Here)

Copyright 2008 - 2018 ARCAT, Inc. - All rights reserved

** NOTE TO SPECIFIER ** Savaria ; residential and commercial elevators and lifts.
 .
 This section is based on the products of Savaria, which is located at:
2 Walker Drive  
Brampton, ON, Canada L6T 5E1
Toll Free Tel: 800-661-5112
Tel: 905-791-5555
Fax: 905-791-2222
Email: request info
Web: www.savaria.com

As a leading designer and manufacturer of residential elevators, luxury home elevators, commercial elevators and lifts for over 30 years, Savaria Lifts has thousands of satisfied customers to thank for their business.
 Our global operation continuously seeks to advance manufacturing processes in our own modern facilities, allowing us to offer exceptional value and shorter lead times, while never compromising product quality, safety or reliability.
 As an active member of many trade associations, we are committed to the ongoing support of its customers and dealers alike. Authorized dealers are carefully selected for their knowledge and experience, kept up-to-date with the latest technical and training sessions, and supported with our expert customer service.
Commercial Wheelchair Lifts:

Savaria Prolift SCL: A fully enclosed Commercial Lift that provides an economical means of vertical transportation for the physically disabled. It has a reliable, quiet, and smooth operation while serving from two to four floors.

- GENERAL

  - SECTION INCLUDES

    - Commercial wheelchair lifts.

  - RELATED SECTIONS

** NOTE TO SPECIFIER ** Delete any sections below not relevant for elevator products; add others as required.

    - Division 16 Sections for electrical service for elevators to and including disconnect and fused switches at machine room.

    - Division 16 Sections for standby power source, transfer switch, and connection from auxiliary contacts in transfer switch to controller.

    - Division 16 Section "Voice and Data Communication Cabling" for telephone service to elevators.

    - Section 03300 - Cast-in-Place Concrete: Concrete for elevator machine foundation, and pit.

    - Section 06100 - Rough Carpentry: Hoistway framing, building-in hoistway door frames and overhead hoist beams.

    - Section 08210 - Wood Doors: Hoistway doors.

    - Section 08710 - Door Hardware.

    - Section 09260 - Gypsum Board Assemblies: Gypsum shaft walls.

    - Section 09650 - Resilient Flooring: Floor finish in cab.

    - Section 09686 - Carpet: Floor finish in cab.

    - Section 09900 - Paints and Coatings: Interior transparent wood finish in cab.

    - Section 13850 - Detection and Alarm: Fire and smoke detectors and interconnecting devices.

  - REFERENCES

** NOTE TO SPECIFIER ** Delete references from the list below that are not required.

    - American National Standards Institute (ANSI) B-29.2 - Chain Standards for Inverted Tooth (Silent) Chains and Sprockets.

    - American Society of Mechanical Engineers (ASME) A17.1 - Safety Code for Elevators and Escalators.

    - American Society of Mechanical Engineers (ASME) A18.1 - Safety Standard for Platform and Stairway Chair Lifts.

    - CSA B44.1 - Elevator and Escalator Electrical Equipment.

    - CSA B355 - Lifts for Persons with Physical Disabilities.

    - CSA B613 - Private Residence Lifts for Persons with Physical Disabilities.

    - U.S. Architectural & Transportation Barriers Compliance Board's "Americans with Disabilities Act (ADA), Accessibility Guidelines for Buildings and Facilities (ADAAG)".

    - ICC/ANSI A117.1 - Accessible and Usable Buildings and Facilities.

    - NFPA 70 - National Electric Code.

    - CSA - National Electric Code.

  - REQUIREMENTS OF REGULATORY AGENCIES:

    - Fabricate and install work in compliance with applicable jurisdictional authorities.

    - File shop drawings and submissions with local authorities as the information is made available. Company pre-inspection and jurisdictional authority inspections and permits are to be made on timely basis as required.

  - SUBMITTALS

    - Submit under provisions of Section 01300.

    - Product Data: Manufacturer's data sheets on each product to be used, including:

      - Preparation instructions and recommendations.

      - Storage and handling requirements and recommendations.

      - Installation methods.

    - Shop Drawings: Provide a complete layout of lift equipment detailing dimensions and clearances as required.

** NOTE TO SPECIFIER ** Delete selection samples if colors have already been selected.

    - Selection Samples: For each finish product specified requiring selection of color or finish, two complete sets of color charts representing manufacturer's full range of available colors and patterns.

  - QUALITY ASSURANCE

    - Installer Qualifications:

      - Skilled tradesmen shall be employees of the installing contractor approved by the manufacturer, with demonstrated ability to perform the work on a timely basis.

      - Execute work of this section only by a company that has adequate product liability insurance.

  - DELIVERY, STORAGE, AND HANDLING

    - Store products in manufacturer's unopened packaging until ready for installation.

    - Store and dispose of solvent-based materials, and materials used with solvent-based materials, in accordance with requirements of local authorities having jurisdiction.

  - PROJECT CONDITIONS

    - Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install systems under environmental conditions outside manufacturer's absolute limits.

  - WARRANTY

    - Coverage - this warranty applies to the repair or replacement, at Manufacturer's option, of parts that fail due to defective material or workmanship. Manufacturer may, at its option, provide factory reconditioned parts. This warranty is provided to the Authorized Dealer on behalf of the final purchaser of the product and is not transferable. The Manufacturer's warranty does not cover labor charges for the removal, repair or replacement of warranty parts but such costs may be covered for a period of time by Authorized Dealer's warranty, which is provided to purchaser separately.

      - The manufacturer shall offer a 36-month limited warranty on parts from date of shipment.

- PRODUCTS

  - MANUFACTURERS

    - Acceptable Manufacturer:  Savaria, which is located at: 2 Walker Drive, Brampton, ON, Canada, L6T 5E1; Toll Free Tel: 800-661-5112; Tel: 905-791-5555; Fax:  905-791-2222; Email: request info; Web: www.savaria.com

** NOTE TO SPECIFIER ** Delete one of the following two paragraphs; coordinate with requirements of Division 1 section on product options and substitutions.

    - Substitutions: Not permitted.

    - Requests for substitutions will be considered in accordance with provisions of Section 01600.

  - COMMERCIAL WHEELCHAIR LIFT

    - Commercial Wheelchair Lifts: Savaria Prolift.

    - Hydraulic Wheelchair Platform Lift: The lift described here, manufactured by Savaria Lifts Inc, is a vertical wheelchair lift consisting of a roped hydraulic drive with a lifting platform. The platform is made to accommodate a wheelchair user or a person with impaired mobility.

    - Work described in this section includes providing equipment, incidental material and labor required for complete, operable roped hydraulic wheelchair lift installation. Lifts shall be erected, installed, adjusted, tested and placed in operation by lift system manufacturer, or manufacturer's authorized installer.

- Lifts shall be in accordance:

** NOTE TO SPECIFIER ** Select code and accessibility standard required.

- ASME A18.1 and ADAAG compliant (USA)

- ASME A18.1 and A117.1 compliant (USA)

- ASME 18.1 only (USA)

- CSA B355 (Canada)

    - The following preparatory work to receive the lifts specified in this section is part of the work of other sections:

      - Permanent 220 VAC, 40 amp single phase power or 208 VAC, 30 amp, 3 phase power to operate lift to be provided from a lockable fused/cartridge type disconnect switch with auxiliary contacts for battery operation. 110 VAC, 15 amp single phase power to operate the lighting circuit. Refer to drawings for permanent power specifications and location of disconnects. Temporary power may be provided to expedite installation of lift.

      - Provide a plumb and square hoistway with smooth interior surfaces, including fascias or furring of the hoistway interior.

      - Provide rough openings per lift subcontractor's shop drawings.

      - Provide substantial, level pit floor slab as indicated on the lift contractor's shop drawings.

    - Characteristics:

      - Rated Load:

** NOTE TO SPECIFIER ** Delete rated load if not required.

- 750 lbs   (350 kg)

- 1050 lbs (476 kg) – Accepted under ASME A18.1 2008 & 2011 code and Canada.

- 1400 lbs (635 kg) – Canada only

      - Rated Speed: 30 fpm (0.15 m/s).

      - Platform Configuration:

** NOTE TO SPECIFIER ** Delete platform configuration not required.

- Enter/exit same side.

- Enter/exit front/rear.

- 90 degree exit.

      - Car Dimensions:

** NOTE TO SPECIFIER ** Delete platform size if not required.

For a 90 degree application in the USA platform size “d” must be selected.

For a 90 degree application in Canada platform size “d” or “e” must be selected.

- 36 inches W by 48 inches D (914 mm by 1219 mm).

- 36 inches W by 54 inches D (914 mm by 1371 mm).

- 36 inches W by 60 inches D (914 mm by 1524 mm).

- 42 inches W by 60 inches D (1067 mm by 1524 mm).

- 48 inches W by 60 inches D (1219 mm by 1524 mm). – Canada Only

- 35 inches W by 84 inches D (889 mm by 2134 mm).   – Canada Only

      - Levels Serviced:

** NOTE TO SPECIFIER ** Delete levels not required.

- 2

- 3

- 4

** NOTE TO SPECIFIER ** Please enter travel height

      - Travel: ______ feet. * Maximum of 14’ in US and 23’ in Canada.

      - Pit Depth:

** NOTE TO SPECIFIER ** Please select pit depth. 8” pit depth is used for units with a rated capacity of 750 lbs (350 kg) or 1050 lbs (476 kg) and a 14” pit depth is used for units with a rated capacity of 1400 lbs (635 kg).

- 8”

- 14”

      - Operation: Constant pressure.

      - Power Supply:

** NOTE TO SPECIFIER ** Select power supply and delete the one not required.

- 220 Volt, 1 Phase, 40 Amps

- 208 Volt, 3 Phase, 30 Amps

      - Drive System: 2:1 roped hydraulic.

      - Paint: Powder coat finish.

      - Emergency Power: Battery operation in down direction.

      - Controller: Electronic.

      - Motor/Pump: 220VAC, 5HP max.

      - Manual Lowering: Located inside the lockable hydraulic tank in the machine room.

    - Car Enclosure:

      - Wall Finish:

** NOTE TO SPECIFIER ** Delete walls not required.

- MDF (Standard)

- Durable Melamine wall panels (Standard from Manufacturers Chart).

- Plastic Laminate Panels (Optional from Manufacturers Chart)

- Steel Cab in Architectural White or Black (35” x 84” Car Only)

      - Ceiling Finish: White egg-crate ceiling with four recessed incandescent down lights.

      - Clear anodized aluminum car trim.

      - Hands free telephone integrated in COP.

      - Handrail: A single stainless steel handrail, with 1-1/2 inch (38 mm) diameter rail and with both ends returned to the side guard, shall be located on the control wall of the cab.

      - Control Panel: Stainless steel control panel with tactile identifications (keyed stations).

      - Cab Floor: Unfinished 3/4" inch (19 mm) plywood sub-flooring

      - Cab Floor Mat or Recess:

** NOTE TO SPECIFIER ** Delete floor recesses and/or covering not required below.

        - Cover plywood sub-flooring with Anti-Skid Mat 1/8 inch (3 mm) thick

        - Recess plywood sub-flooring by 1/8 inch (3 mm)

        - Recess plywood sub-flooring by ¼ inch (6 mm)

        - Recess plywood sub-flooring by 3/8 inch (9.5 mm)

        - Recess plywood sub-flooring by ½ inch (12.7 mm)

        - Recess plywood sub-flooring by 5/8 inch (16 mm)

    - Hoistway Doors:

      - First Landing door:

        - 80” High 1-1/2 hour UL/ULC fire rated assembly.

        - Flush closing operation with hoistway side.

        - Operation

** NOTE TO SPECIFIER ** Select either a manual or automatic door and delete option not required. Automatic doors should be used on the following platform configurations to meet ADA and ANSI A117.1: 90 Degree, Enter/Exit Same Side and applications with more than 2 stops.

- Manual – with hydraulic closer

- Automatic - Concealed 24 volt door opener with battery back-up.

        - Door Width

** NOTE TO SPECIFIER ** Select either a 36” or 42” wide door and delete the option not required. A 42” wide door should be used on the 90 degree side only. 42” doors can also be used on the narrow side of platforms with a width of 42”.

- 36 inches (889 mm) clear opening.

- 42 inches (1067 mm) clear opening

        - Concealed electro/mechanical interlock.

        - Concealed hinges.

NOTE TO SPECIFIER ** Delete second landing if not required.

      - Second Landing door:

        - 80” High 1-1/2 hour UL/ULC fire rated assembly.

        - Flush closing operation with hoistway side.

        - Operation

** NOTE TO SPECIFIER ** Select either a manual or automatic door and delete option not required. Automatic doors should be used on the following platform configurations to meet ADA and ANSI A117.1: 90 Degree, Enter/Exit Same Side and applications with more than 2 stops.

- Manual – with hydraulic closer

- Automatic - Concealed 24 volt door opener with battery back-up.

        - Door Width

** NOTE TO SPECIFIER ** Select either a 36” or 42” wide door and delete the option not required. A 42” wide door should be used on the 90 degree side only. 42” doors can also be used on the narrow side of platforms with a width of 42”.

- 36 inches (889 mm) clear opening.

- 42 inches (1067 mm) clear opening

        - Concealed electro/mechanical interlock.

        - Concealed hinges.

** NOTE TO SPECIFIER ** Delete third landing if not required.

      - Third Landing door:

        - 80” High 1-1/2 hour UL/ULC fire rated assembly.

        - Flush closing operation with hoistway side.

        - Operation

** NOTE TO SPECIFIER ** Select either a manual or automatic door and delete option not required. Automatic doors should be used on the following platform configurations to meet ADA and ANSI A117.1: 90 Degree, Enter/Exit Same Side and applications with more than 2 stops.

- Manual – with hydraulic closer

- Automatic - Concealed 24 volt door opener with battery back-up.

        - Door Width

** NOTE TO SPECIFIER ** Select either a 36” or 42” wide door and delete the option not required. A 42” wide door should be used on the 90 degree side only. 42” doors can also be used on the narrow side of platforms with a width of 42”.

- 36 inches (889 mm) clear opening.

- 42 inches (1067 mm) clear opening

        - Concealed electro/mechanical interlock.

        - Concealed hinges.

      - Upper Landing door:

        - 80” High 1-1/2 hour UL/ULC fire rated assembly.

        - Flush closing operation with hoistway side.

        - Operation

** NOTE TO SPECIFIER ** Select either a manual or automatic door and delete option not required. Automatic doors should be used on the following platform configurations to meet ADA and ANSI A117.1: 90 Degree, Enter/Exit Same Side and applications with more than 2 stops.

- Manual – with hydraulic closer

- Automatic - Concealed 24 volt door opener with battery back-up.

        - Door Width

** NOTE TO SPECIFIER ** Select either a 36” or 42” wide door and delete the option not required. A 42” wide door should be used on the 90 degree side only. 42” doors can also be used on the narrow side of platforms with a width of 42”.

- 36 inches (889 mm) clear opening.

- 42 inches (1067 mm) clear opening

        - Concealed electro/mechanical interlock.

        - Concealed hinges.

    - Car Operating Panel:

- Car operating panel shall consist of constant pressure buttons, emergency stop/alarm button, on/off key switch (when applicable) and emergency light mounted on a removable stainless steel panel (Type 304 #4 Stainless Steel Finish).

- Digital floor indicator in cab.

- Emergency Operation - The car shall be equipped with a battery operated light fixture, emergency battery lowering device and alarm in case of normal building supply failure. The battery shall be the rechargeable type with an automatic recharging system. A manual lowering device shall be located inside the lockable hydraulic tank in the machine room.

    - Pumping Unit and Control:

      - The pumping unit and control shall be in a separate machine room. The controller and pump unit shall be pre-wired and tested prior to shipment. Pump unit shall incorporate the following features :

      - Smooth stops at each landing.

      - Submersible pump and motor.

      - Adjustable pressure relief valve.

      - Manually operable down valve to lower lift in the event of an emergency. This valve shall be activated from the machine room.

      - Pressure gauge isolating valve, manually operable.

      - Gate valve to isolate cylinder from pump unit.

      - Electro Proportional valve for accurate and smooth starts and stops in both directions.

      - Emergency lowering by battery power, from the car control.

    - Cylinder And Plunger:

      - The cylinder shall be constructed of a steel pipe of sufficient thickness and suitable safety margin. The top of the cylinder shall be equipped with a cylinder head with an internal guide ring and self-adjusting packing.

      - The plunger shall be constructed of a solid steel shaft of proper diameter machined true and smooth. The plunger shall be provided with a stop electrically welded to the bottom to prevent the plunger from leaving the cylinder.

    - Aircraft Cable: Two, Minimum breaking strength 14,400 lb (6545 kg) each.

    - Leveling Device:

      - The lift shall be provided with an anti-creep device which will maintain the carriage level within 1/2 inch (12 mm) of each landing.

      - All limit switch and leveling device switches shall be located in a position to be inaccessible to unauthorized persons.

    - Guide Yoke: The 2:1 guide yoke assembly shall be supplied with one (1) sheaves, guide shoes, bearings and guards.

    - Call Stations: Provide flush, surface or door frame mounted landing call/send stations.

- Call stations will be:

** NOTE TO SPECIFIER ** Select required key switch option below and delete items not required.

- Keyless

- Keyed (removable in off position)

- Keyed (removable in on/off position)

    - Terminal Stopping Devices: Normal terminal stopping devices shall be provided at top and bottom of runway to stop the car positively and automatically. Micro switches shall not be used.

    - Guide Rails: Steel 8 lb per foot guide rails to guide the platform and sling.

    - Car Sling: Car sling shall be fabricated from steel with adequate bracing to support the platform and car enclosure. Guide shoes shall be mounted on the top and bottom of the car sling to engage the guide rails.

    - Wiring: All wiring and electrical connections shall comply with applicable codes. Insulated wiring shall have flame-retardant and moisture-proof outer covering and shall be run in conduit or electrical wire ways if located outside the unit enclosure. Quick disconnect harnesses shall be used when possible.

- EXECUTION

  - EXAMINATION

    - Do not begin installation until hoistway and machine room has been properly prepared.

    - Site dimensions shall be taken to verify that tolerances and clearances have been maintained and meet local regulations.

    - If substrate preparation is the responsibility of another installer, notify Architect of unsatisfactory preparation before proceeding.

  - PREPARATION

    - Clean surfaces thoroughly prior to installation.

    - Prepare surfaces using the methods recommended by the manufacturer for achieving the best result for the substrate under the project conditions.

** NOTE TO SPECIFIER ** Delete if not required.

  - ELEVATOR INSTALLATION

    - Install in accordance with manufacturer's instructions.

    - Install the components of the elevator system that are required and that are required by jurisdictional authorities to license the elevator.

    - Trained employees of the elevator contractor shall perform installation work.

    - Adjust elevator for proper operation and clean unit thoroughly.

    - Instruct users in operating procedures and owner's maintenance person in trouble-shooting and maintenance procedures.

** NOTE TO SPECIFIER ** Delete if not required.

  - LIFT INSTALLATION

    - Install all the components of the lift system that are specified in this section to be provided, and that are required by jurisdictional authorities to license the lift.

    - Trained employees of the lift contractor shall perform all installation work of this section.

    - Adjust lift for proper operation and clean unit thoroughly.

    - Instruct users in operation procedures and Owner's maintenance person in trouble-shooting and maintenance procedures.

  - PROTECTION

    - Protect installed products until completion of project.

    - Touch-up, repair or replace damaged products before Substantial Completion.

END OF SECTION